## Sayfa1
Turbine_ID | Component | Timestamp | Remarks
T01 | GEARBOX | 2016-07-18T02:10:00+00:00 | Gearbox pump damaged
T06 | GENERATOR | 2016-07-11T19:48:00+00:00 | Generator replaced
T06 | GENERATOR | 2016-07-24T17:01:00+00:00 | Generator temperature sensor failure
T06 | GENERATOR | 2016-09-04T08:08:00+00:00 | High temperature generator error
T06 | GENERATOR | 2016-10-27T16:26:00+00:00 | Generator replaced
T06 | GENERATOR | 2016-10-02T17:08:00+00:00 | Refrigeration system and temperature sensors in generator replaced
T06 | HYDRAULIC_GROUP | 2016-04-04T18:53:00+00:00 | Error in pitch regulation
T07 | GENERATOR_BEARING | 2016-04-30T12:40:00+00:00 | High temperature in generator bearing (replaced sensor)
T07 | TRANSFORMER | 2016-07-10T03:46:00+00:00 | High temperature transformer
T07 | TRANSFORMER | 2016-08-23T02:21:00+00:00 | High temperature transformer. Transformer refrigeration repaired
T09 | GEARBOX | 2016-10-11T08:06:00+00:00 | Gearbox repaired
T09 | GENERATOR_BEARING | 2016-06-07T16:59:00+00:00 | High tempemperature generator bearing
T09 | GENERATOR_BEARING | 2016-08-22T18:25:00+00:00 | High temperature generator bearing
T09 | GENERATOR_BEARING | 2016-10-17T09:19:00+00:00 | Generator bearings replaced
T11 | GENERATOR | 2016-03-03T19:00:00+00:00 | Electric circuit error in generator
T11 | HYDRAULIC_GROUP | 2016-10-17T17:44:00+00:00 | Hydraulic group error in the brake circuit